## Example Modbus Antares Station
Project: |  |  | Antares Sample Station
Antares Station: |  |  | Antares
Location:
Host-Com: |  |  | Modbus-TCP
IP-Address: |  |  | 192.168.1.150
SUB-Net-Mask: |  |  | 255.255.255.0
Project Editor: |  |  | O. Korb
Date: |  |  | 2014-01-31
Module | Terminal block | Module Type | Modbus Input Address | Input Signal | Bit | Modbus Output Address | Output Signal | Bit | Modbus Status Address | Terminal | Connection | Name of Signal | Cable name | Cable description from - to | Cable type | Cable dim.
0 | Modbus | Junction |  |  | - |  |  | - | - |  |  | ANTARES ZONE 1 CAB. - FS44 |  | ANTARES ZONE 1 CAB. - FS44 | Modbus
0 | PWR | Junction | - | - | - | - | - | - | - |  |  | Antares cabinet Rail Control Unit |  | DC31 C24 - Antares cabinet Rail Control Unit | YOZp | 2x2,5
1 | X1 | 16DI | 00000 | Digital | 0 |  |  |  |  | 1 | 1+ 1- | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X1 |  | 00000 | Digital | 1 |  |  |  |  | 2 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X2 |  | 00000 | Digital | 2 |  |  |  |  | 3 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X2 |  | 00000 | Digital | 3 |  |  |  |  | 4 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X3 |  | 00000 | Digital | 4 |  |  |  |  | 5 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X3 |  | 00000 | Digital | 5 |  |  |  |  | 6 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X4 |  | 00000 | Digital | 6 |  |  |  | 30000 | 7 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X4 |  | 00000 | Digital | 7 |  |  |  | 30001 | 8 |  | digital input | -W100 | Antares digital Input | YOZc | 1x2x0,5
1 | X5 |  | 00000 | Digital | 8 |  |  |  | 30002 | 9 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X5 |  | 00000 | Digital | 9 |  |  |  |  | 10 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X6 |  | 00000 | Digital | 10 |  |  |  |  | 11 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X6 |  | 00000 | Digital | 11 |  |  |  |  | 12 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X7 |  | 00000 | Digital | 12 |  |  |  |  | 13 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X7 |  | 00000 | Digital | 13 |  |  |  |  | 14 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X8 |  | 00000 | Digital | 14 |  |  |  |  | 15 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
1 | X8 |  | 00000 | Digital | 15 |  |  |  |  | 16 |  | digital input | -W101 | Antares digital Input | YOZc | 1x2x0,5
2 | X1 | 16DI | 00001 | Digital | 0 |  |  |  |  | 1 |  | digital input | -W201 | Antares digital Input | YOZc | 1x2x0,5
2 | X1 |  | 00001 | Digital | 1 |  |  |  |  | 2 |  | digital input | -W202 | Antares digital Input | YOZc | 1x2x0,5
2 | X2 |  | 00001 | Digital | 2 |  |  |  |  | 3 |  | digital input | -W203 | Antares digital Input | YOZc | 1x2x0,5
2 | X2 |  | 00001 | Digital | 3 |  |  |  |  | 4 |  | digital input | -W204 | Antares digital Input | YOZc | 1x2x0,5
2 | X3 |  | 00001 | Digital | 4 |  |  |  |  | 5 |  | digital input | -W205 | Antares digital Input | YOZc | 1x2x0,5
2 | X3 |  | 00001 | Digital | 5 |  |  |  |  | 6 |  | digital input | -W206 | Antares digital Input | YOZc | 1x2x0,5
2 | X4 |  | 00001 | Digital | 6 |  |  |  | 30003 | 7 |  | digital input | -W207 | Antares digital Input | YOZc | 1x2x0,5
2 | X4 |  | 00001 | Digital | 7 |  |  |  | 30004 | 8 |  | digital input | -W208 | Antares digital Input | YOZc | 1x2x0,5
2 | X5 |  | 00001 | Digital | 8 |  |  |  | 30005 | 9 |  | digital input | -W209 | Antares digital Input | YOZc | 1x2x0,5
2 | X5 |  | 00001 | Digital | 9 |  |  |  |  | 10 |  | digital input | -W210 | Antares digital Input | YOZc | 1x2x0,5
2 | X6 |  | 00001 | Digital | 10 |  |  |  |  | 11 |  | digital input | -W211 | Antares digital Input | YOZc | 1x2x0,5
2 | X6 |  | 00001 | Digital | 11 |  |  |  |  | 12 |  | digital input | -W212 | Antares digital Input | YOZc | 1x2x0,5
2 | X7 |  | 00001 | Digital | 12 |  |  |  |  | 13 |  | digital input | -W213 | Antares digital Input | YOZc | 1x2x0,5
2 | X7 |  | 00001 | Digital | 13 |  |  |  |  | 14 |  | digital input | -W214 | Antares digital Input | YOZc | 1x2x0,5
2 | X8 |  | 00001 | Digital | 14 |  |  |  |  | 15 |  | digital input | -W215 | Antares digital Input | YOZc | 1x4x0,5 (1,2)
2 | X8 |  | 00001 | Digital | 15 |  |  |  |  | 16 |  | digital input | -W216 | Antares digital Input | YOZc | 1x4x0,5 (3,4)
3 | X1 | 8AI | 00002 | Analog | [5 empty] | 1 |  | 4-20mA Input, Channel 1 | -W300 | Antares analog Input | YOZc | 1x2x0,5
3 | X1 |  | 00003 | Analog | W |  |  |  |  | 2 |  | 4-20mA Input, Channel 2 | -W301 | Antares analog Input | YOZc | 1x2x0,5
3 | X2 |  | 00004 | Analog | o |  |  |  | 30006 | 3 |  | 4-20mA Input, Channel 3 | -W302 | Antares analog Input | YOZc | 1x2x0,5
3 | X2 |  | 00005 | Analog | r |  |  |  | 30007 | 4 |  | 4-20mA Input, Channel 4 | -W303 | Antares analog Input | YOZc | 1x2x0,5
3 | X3 |  | 00006 | Analog | d |  |  |  | 30008 | 5 |  | 4-20mA Input, Channel 5 | -W304 | Antares analog Input | YOZc | 1x2x0,5
3 | X3 |  | 00007 | Analog | s |  |  |  |  | 6 |  | 4-20mA Input, Channel 6 | -W305 | Antares analog Input | YOZc | 1x2x0,5
3 | X4 |  | 00008 | Analog | [5 empty] | 7 |  | 4-20mA Input, Channel 7 | -W306 | Antares analog Input | YOZc | 1x2x0,5
3 | X4 |  | 00009 | Analog | [5 empty] | 8 |  | 4-20mA Input, Channel 8 | -W307 | Antares analog Input | YOZc | 1x2x0,5
4 | X1 | 8AI | 00010 | Analog | [5 empty] | 1 |  | 4-20mA Input, Channel 1 | -W400 | Antares analog Input | YOZc | 1x2x0,5
4 | X1 |  | 00011 | Analog | W |  |  |  |  | 2 |  | 4-20mA Input, Channel 2 | -W401 | Antares analog Input | YOZc | 1x2x0,5
4 | X2 |  | 00013 | Analog | o |  |  |  | 30009 | 3 |  | 4-20mA Input, Channel 3 | -W402 | Antares analog Input | YOZc | 1x2x0,5
4 | X2 |  | 00014 | Analog | r |  |  |  | 30010 | 4 |  | 4-20mA Input, Channel 4 | -W403 | Antares analog Input | YOZc | 1x2x0,5
4 | X3 |  | 00015 | Analog | d |  |  |  | 30011 | 5 |  | 4-20mA Input, Channel 5 | -W404 | Antares analog Input | YOZc | 1x2x0,5
4 | X3 |  | 00016 | Analog | s |  |  |  |  | 6 |  | 4-20mA Input, Channel 6 | -W405 | Antares analog Input | YOZc | 1x2x0,5
4 | X4 |  | 00017 | Analog | [5 empty] | 7 |  | 4-20mA Input, Channel 7 | -W406 | Antares analog Input | YOZc | 1x2x0,5
4 | X4 |  | 00018 | Analog | [5 empty] | 8 |  | 4-20mA Input, Channel 8 | -W407 | Antares analog Input | YOZc | 1x2x0,5
5 | X1 | 8AI | 00019 | Analog | [5 empty] | 1 |  | 4-20mA Input, Channel 1 | -W500 | Antares analog Input | YOZc | 1x2x0,5
5 | X1 |  | 00020 | Analog | W |  |  |  |  | 2 |  | 4-20mA Input, Channel 2 | -W501 | Antares analog Input | YOZc | 1x2x0,5
5 | X2 |  | 00021 | Analog | o |  |  |  | 30012 | 3 |  | 4-20mA Input, Channel 3 | -W502 | Antares analog Input | YOZc | 1x2x0,5
5 | X2 |  | 00022 | Analog | r |  |  |  | 30013 | 4 |  | 4-20mA Input, Channel 4 | -W503 | Antares analog Input | YOZc | 1x2x0,5
5 | X3 |  | 00023 | Analog | d |  |  |  | 30014 | 5 |  | 4-20mA Input, Channel 5 | -W504 | Antares analog Input | YOZc | 1x2x0,5
5 | X3 |  | 00024 | Analog | s |  |  |  |  | 6 |  | 4-20mA Input, Channel 6 | -W505 | Antares analog Input | YOZc | 1x2x0,5
5 | X4 |  | 00025 | Analog | [5 empty] | 7 |  | Spare | Spare
5 | X4 |  | 00026 | Analog | [5 empty] | 8 |  | 4-20mA Input, Channel 8 | -W506 | Antares analog Input | YOZc | 1x2x0,5
6 | X1 | 8AI | 00027 | Analog | [5 empty] | 1 |  | 4-20mA Input, Channel 1 | -W600 | Antares analog Input | YOZc | 1x2x0,5
6 | X1 |  | 00028 | Analog | W |  |  |  |  | 2 |  | Spare | Spare
6 | X2 |  | 00029 | Analog | o |  |  |  | 30015 | 3 |  | 4-20mA Input, Channel 3 | -W602 | Antares analog Input | YOZc | 1x2x0,5
6 | X2 |  | 00030 | Analog | r |  |  |  | 30016 | 4 |  | 4-20mA Input, Channel 4 | -W603 | Antares analog Input | YOZc | 1x2x0,5
6 | X3 |  | 00031 | Analog | d |  |  |  | 30017 | 5 |  | Spare | Spare
6 | X3 |  | 00032 | Analog | s |  |  |  |  | 6 |  | 4-20mA Input, Channel 6 | -W604 | Antares analog Input | YOZc | 1x2x0,5
6 | X4 |  | 00033 | Analog | [5 empty] | 7 |  | 4-20mA Input, Channel 7 | -W605 | Antares analog Input | YOZc | 1x2x0,5
6 | X4 |  | 00034 | Analog | [5 empty] | 8 |  | Spare | Spare
7 | X1 | 8AI | 00035 | Analog | [5 empty] | 1 |  | 4-20mA Input, Channel 1 | -W700 | Antares analog Input | YOZc | 1x2x0,5
7 | X1 |  | 00036 | Analog | W |  |  |  |  | 2 |  | 4-20mA Input, Channel 2 | -W701 | Antares analog Input | YOZc | 1x2x0,5
7 | X2 |  | 00037 | Analog | o |  |  |  | 30018 | 3 |  | 4-20mA Input, Channel 3 | -W702 | Antares analog Input | YOZc | 1x2x0,5
7 | X2 |  | 00038 | Analog | r |  |  |  | 30019 | 4 |  | Spare | Spare | Spare
7 | X3 |  | 00039 | Analog | d |  |  |  | 30020 | 5 |  | Spare | Spare | Spare
7 | X3 |  | 00040 | Analog | s |  |  |  |  | 6 |  | Spare | Spare | Spare
7 | X4 |  | 00041 | Analog | [5 empty] | 7 |  | Spare | Spare | Spare
7 | X4 |  | 00042 | Analog | [5 empty] | 8 |  | Spare | Spare | Spare
8 | X1 | 8DI | 00043 | Digital | 0 |  |  |  |  | 1 |  | digital input | -W800 | Antares analog Input | YOZc | 1x2x0,5
8 | X1 |  | 00043 | Digital | 1 |  |  |  |  | 2 |  | digital input | -W801 | Antares analog Input | YOZc | 1x2x0,5
8 | X2 |  | 00043 | Digital | 2 |  |  |  |  | 3 |  | digital input | -W802 | Antares analog Input | YOZc | 1x2x0,5
8 | X2 |  | 00043 | Digital | 3 |  |  |  |  | 4 |  | Spare | Spare | Spare
8 | X3 |  | 00043 | Digital | 4 |  |  |  |  | 5 |  | Spare | Spare | Spare
8 | X3 |  | 00043 | Digital | 5 |  |  |  |  | 6 |  | Spare | Spare | Spare
8 | X4 |  | 00043 | Digital | 6 |  |  |  | 30021 | 7 |  | Spare | Spare | Spare
8 | X4 |  | 00043 | Digital | 7 |  |  |  | 30022 | 8 |  | Spare | Spare | Spare
8 | X5 |  | 00043 | Digital | 8 |  |  |  | 30023 | 9 |  | Spare | Spare | Spare
8 | X5 |  | 00043 | Digital | 9 |  |  |  |  | 10 |  | Spare | Spare | Spare
8 | X6 |  | 00043 | Digital | 10 |  |  |  |  | 11 |  | Spare | Spare | Spare
8 | X6 |  | 00043 | Digital | 11 |  |  |  |  | 12 |  | Spare | Spare | Spare
8 | X7 |  | 00043 | Digital | 12 |  |  |  |  | 13 |  | Spare | Spare | Spare
8 | X7 |  | 00043 | Digital | 13 |  |  |  |  | 14 |  | Spare | Spare | Spare
8 | X8 |  | 00043 | Digital | 14 |  |  |  |  | 15 |  | Spare | Spare | Spare
8 | X8 |  | 00043 | Digital | 15 |  |  |  |  | 16 |  | Spare | Spare | Spare
9 | X1 | 8DO |  |  |  | 10000 | Digital | 1 |  | 1 |  | Digital Output 1 | -W900 | ANTARES digital Output | YOZc | 1x16x0,5
9 | X1 |  |  |  |  | 10000 | Digital | 2 |  | 2 |  | Digital Output 2 | -W900 | ANTARES digital Output | YOZc | 1x16x0,5
9 | X2 |  |  |  |  | 10000 | Digital | 3 |  | 3 |  | Digital Output 3 | -W900 | ANTARES digital Output | YOZc | 1x16x0,5
9 | X2 |  |  |  |  | 10000 | Digital | 4 |  | 4 |  | Spare | -W900 | Spare
9 | X3 |  |  |  |  | 10000 | Digital | 5 |  | 5 |  | Spare | -W900 | Spare
9 | X3 |  |  |  |  | 10000 | Digital | 6 |  | 6 |  | Spare | -W900 | Spare
9 | X4 |  |  |  |  | 10000 | Digital | 7 | 30024 | 7 |  | Spare | -W900 | Spare
9 | X4 |  |  |  |  | 10000 | Digital | 8 | 30025 | 8 |  | Spare | -W900 | Spare
9 | X5 |  |  |  |  | 10000 |  |  | 30026 | 9 |  |  | don´t care
9 | X5 |  |  |  |  | 10000 |  |  |  | 10 |  |  | don´t care
9 | X6 |  |  |  |  | 10000 |  |  |  | 11 |  |  | don´t care
9 | X6 |  |  |  |  | 10000 |  |  |  | 12 |  |  | don´t care
9 | X7 |  |  |  |  | 10000 |  |  |  | 13 |  |  | don´t care
9 | X7 |  |  |  |  | 10000 |  |  |  | 14 |  |  | don´t care
9 | X8 |  |  |  |  | 10000 |  |  |  | 15 |  |  | don´t care
9 | X8 |  |  |  |  | 10000 |  |  |  | 16 |  |  | don´t care
10 | X1 | 4AIO |  |  |  | 10001 | analog | WORD | 30027 | 1 |  | 4-20mA as Output, Channel 1 | Spare | ANTARES analog Output | JYSTY | 1x2x0,5
10 | X2 |  |  |  |  | 10002 | analog |  | 30028 | 2 |  | 4-20mA as Output, Channel 2 | Spare | ANTARES analog Output | JYSTY | 1x2x0,5
10 | X3 |  |  |  |  | 10003 | analog |  | 30029 | 3 |  | 4-20mA as Output, Channel 3 | Spare | ANTARES analog Output | JYSTY | 1x2x0,5
10 | X4 |  |  |  |  | 10004 | analog |  |  | 4 |  | Spare | Spare | Spare
Note on G14: Frode Pedersen Bergsager: Either bit 0-15 or1-16
Note on G86: Frode Pedersen Bergsager: Either bit 0-15 or1-16
Note on G102: Frode Pedersen Bergsager: Either bit 0-15 or1-16
Note on J14: Frode Pedersen Bergsager: Either bit 0-15 or1-16
Note on J86: Frode Pedersen Bergsager: Either bit 0-15 or1-16
Note on J102: Frode Pedersen Bergsager: Either bit 0-15 or1-16

## ModbusTCP Addresses
Addresses of a Modbus TCP Station
| Module | Input | Output | Status
| 8DI (no counter) | 1 Word |  | 3 Word
| 8DI (one counter) | 3 Word | 1 Word | 3 Word
| 8DI (two counter) | 5 Word | 1 Word | 3 Word
| 16DI | 1 Word |  | 3 Word
| 8DO |  | 1 Word | 3 Word
| 8DO SCL |  | 1 Word | 3 Word
| 8AI/8AIH | 8 Word |  | 3 Word
| 4AIO/4AIOH (4 In, 0 Out) | 4 Word |  | 3 Word
| 4AIO/4AIOH (4 In, 0 Out) | 3 Word | 1 Word | 3 Word
| 4AIO/4AIOH (4 In, 0 Out) | 2 Word | 2 Word | 3 Word
| 4AIO/4AIOH (4 In, 0 Out) | 1 Word | 3 Word | 3 Word
| 4AIO/4AIOH (4 In, 0 Out) |  | 4 Word | 3 Word
| 4TI | 4 Word |  | 3 Word
Example for Inputs:
|  |  | Words | Channel 1 | Channel 2 | Channel 3 | Channel 4 | Channel 5 | Channel 6 | Channel 7 | Channel 8
| 1 | 16DI | 1 | 0
| 2 | 16DI | 1 | 1
| 3 | 8AI | 8 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| 4 | 8AI | 8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
| 5 | 8AI | 8 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| 6 | 8AI | 8 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
| 7 | 8AI | 8 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41
| 8 | 8AI | 8 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
| 9 | 8AI | 8 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57
| 10 | 8AI | 8 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
| 11 | 8DI | 1 | 66
Addresses of Modules Input
0XXXX see sheet on left side
Addresses of Modules Output
1XXXXX see sheet on left side
Addresses of RCU:
20000 RCU Error
20001 reserved
20002 Number of Modules installed
20003 32 register for Moduletypes
every needs one word, hi-byte = main type, low-byte=sub type
Addresses of Module-Status:
3XXXX 3 Word for every Module which is installed
Addresses of coniguration
40000 Timeout register in ms. Standard is 2000ms
Timeout 0ms -> deactivated

## ModbusTCP Address Calculation
Address Calculation Modbus TCP Station
No: | SAP: | Type: | Module | Station contains Number of Modules | Input Words 0XXXXX | Output Words 1XXXX | Address of RCU 20000X | Input Status Module 3XXXXX | RCU Timeout Register 40000 | Input Words Total 0XXXXX | Output Words Total 1XXXXX | Address of RCU Total 20000X | Input Words Status Total 3XXXXX | Timeout Register Total 40000
1 | 290838 | 17-5174-1300 | Ethernet/IP RCU | 1 |  |  | 3 |  | 1 | 0 | 0 | 3 | 0 | 1
2 | 289517 | 17-6143-1001 | 8DO |  |  | 1 | 1 | 3
3 | 308746 | 17-6143-1010 | 8DO/SCL |  |  | 1 | 1 | 3
4 | 289518 | 17-6143-1002 | 8DI:8DI | 1 | 1 |  | 1 | 3 |  | 1 | 0 | 1 | 3
5 | 289518 | 17-6143-1002 | 8DI:1CI7DI |  | 3 | 1 | 1 | 3
6 | 289518 | 17-6143-1002 | 8DI:2CI6DI |  | 5 | 1 | 1 | 3
7 | 289524 | 17-6143-1008 | 16DI | 2 | 1 |  | 1 | 3 |  | 2 | 0 | 2 | 6
8 | 289519 | 17-6143-1003 | 4TI |  | 4 |  | 1 | 3
9 | 289520 | 17-6143-1004/1005 | 8AI/8AIH | 8 | 8 |  | 1 | 3 |  | 64 | 0 | 8 | 24
10 | 289522 | 17-6143-1006/1007 | 4AIO/4AIOH:4AI |  | 4 |  | 1 | 3
11 | 289522 | 17-6143-1006/1007 | 4AIO:3AI1AO |  | 3 | 1 | 1 | 3
12 | 289522 | 17-6143-1006/1007 | 4AIO:2AI2AO |  | 2 | 2 | 1 | 3
13 | 289522 | 17-6143-1006/1007 | 4AIO:1AI3AO |  | 1 | 3 | 1 | 3
14 | 289522 | 17-6143-1006/1007 | 4AIO:4AO |  |  | 4 | 1 | 3
[9 empty] | Total: | 67 | 0 | 14 | 33 | 1

## EthernetIP Address Calculation
Address Calculation Ethernet/IP Station
Bytes of module
No: | SAP: | Type: | Module | Station contains Number of Modules | Output Bytes | Input Bytes | Input Status Module Bytes | Input Status Open Bytes | Input Status Short Bytes | Output Words Total | Input Words Total
1 | 290838 | 17-5174-1300 | Ethernet/IP RCU | 1 | 4 | 4 |  |  |  | 4 | 4
2 | 289517 | 17-6143-1001 | 8DO | 3 | 1 |  | 1 | 1 | 1 | 3 | 9
3 | 308746 | 17-6143-1010 | 8DO/SCL |  | 1 |  | 1 | 1 | 1
4 | 289518 | 17-6143-1002 | 8DI:8DI |  |  | 1 | 1 | 1 | 1
5 | 289518 | 17-6143-1002 | 8DI:1CI7DI |  | 1 | 5 | 1 | 1 | 1
6 | 289518 | 17-6143-1002 | 8DI:2CI6DI |  | 1 | 9 | 1 | 1 | 1
7 | 289524 | 17-6143-1008 | 16DI | 2 |  | 2 | 1 | 2 | 2 | 0 | 14
8 | 289519 | 17-6143-1003 | 4TI |  |  | 8 | 1 | 1 | 1
9 | 289520 | 17-6143-1004/1005 | 8AI/8AIH |  |  | 16 | 1 | 1 | 1
10 | 289522 | 17-6143-1006/1007 | 4AIO/4AIOH:4AI |  |  | 8 | 1 | 1 | 1
11 | 289522 | 17-6143-1006/1007 | 4AIO:3AI1AO | 1 | 2 | 6 | 1 | 1 | 1 | 2 | 9
12 | 289522 | 17-6143-1006/1007 | 4AIO:2AI2AO |  | 4 | 4 | 1 | 1 | 1
13 | 289522 | 17-6143-1006/1007 | 4AIO:1AI3AO |  | 6 | 2 | 1 | 1 | 1
14 | 289522 | 17-6143-1006/1007 | 4AIO:4AO | 3 | 8 |  | 1 | 1 | 1 | 24 | 9
[9 empty] | Total: | 33 | 45